## Airflow
Air Flow
Calculate ▲T (Temperature drop/rise through the heat exchanger).
▲T | = | BTU/H | / | CFM
22.7373 |  | 19424 | / | 791 | 1.08 x CFM (Typical)
Airflow when you know the ▲T, CFM=BTU/h / (1.08 x ▲T).
CFM | = | BTU/H | / | (1.08 x ▲T)
1460.4267 |  | 36277 | / | 23
Airflow required when you know the furnace output and
size of evaporator coil. Size ductwork to larger CFM.
Heating CFM | = | BTU/H
1190 |  | 85000 | @ | 14 | 14 CFM/1000 BTU/h (Typical)
Cooling CFM | = | Tons |  | CFM/Ton
800 |  | 2 | @ | 400 | 400 CFM/Ton (Typical)
Total Sensible Heat. |  | Compare Total Sensible Heat to Furnace BTU intput.
Calculate thermal efficiency.
TSH | = | CFM | X | ▲T
19648.44 |  | 791 | X | 23 | CFM X 1.08 x ▲T
| Furnace BTU Input | 36000 |  | 54.58% | Total System Efficiency
Calculating Duct Losses |  |  | CFM | 1200
|  |  | Attic Air °F | 130 |  |  | Mixed Air 1 °F
[6 empty] | Mixed Air °F | 85.5
BTU/h Loss |  | Return Air °F |  | Supply Air °F |  | Average | Mixed Air 2 °F
12052.8 |  | 74 |  | 63.3 |  | 83.3 | 81.1
| Cooling Loss-33.5% | *Mixed air temps are the average of 2 measurements taken on both sides of blower motor-for best results.
Calculating Filter Face Velocity (Ideally between 250-500 fpm)
| Filter Face Velocity (FFV) | Length |  | Width |  | CFM
230.4 fpm |  | 20 | In | 25 | In | 800
CFM-Electric Heat |  | (Volts x Amps x 3.4141) / (1.08 x ΔT)
|  |  |  | 10800 | Watts
CFM | = | Volts |  | Amps |  | ▲T
1219.3214 |  | 240 |  | 45 |  | 28
Sizing Electric Heat Strips for Heat Pump
KWH | = | WHL |  | Cap 17° |  | Cap 47° | WDT°
6.4948 |  | 36000 |  | 15000 |  | 20000 | 10
Sizing for Entire Load
KWH | = | WHL
10.5479 |  | 36000
WHL = Winter heat loss based on Manual-J
Cap 17° = rated heat pump capacity at 17°
Cap 47° = rated heat pump capacity at 47°
WDT° = Winter design temperature based on Manual-J / Ashrae charts
Clocking a Gas Meter-Thermal Efficiency of a Furnace
| Drive Dial | 2 | Cubic Feet
| Seconds-1 revolution | 80
| Cubic Ft/Hour | 90 | ACFH (Actual Cubic Ft/Hour)
If meter pressure is above 1 psi and a higer elevation
| PSIG @ Meter | 2
| Elevation | 1 | Ft.
| PSIA | 14.6955
| Cubic Ft/Hour@ Burner Tip | 1.1361
| Flow Rate | 107357.2275 | SCFH (Standard Cubic Ft/Hour)
@ 2 PSIG at the meter, customer burns 1.136 cubic feet/hr at the tip
and the adjusted flow rate (SCFH) is 107357.23 Cubic Feet/Hour.
BTU Output |  | Gas
| BTU content of gas | 1050 | 1050 (typical)
| Efficiency of Appliance | 80 | %
| BTU Output | 75600 | ACFH
| BTU Output | 85885.782 | SCFH
Total Sensible Heat Calculation
Estimated or Actual CFM |  | Delta T |  | BTU Output
1500 |  | 50 |  | 81000
|  | Flow Rate (from above) |  | 107357.2275
| Thermal Efficiency | 75.45%
Btu Content of Oil-Thermal Efficiency of a Furnace
Heating Oil
| BTU content of Oil | 138690 | 139,000/gallon (typical)
| Nozzle Firing Rate | 0.55 | @
| Pump Pressure | 135 | psi
| True Firing Rate | 0.64 | gph
| Efficiency of Appliance | 80 | %
| BTU Output | 71009.28
Total Sensible Heat Calculation
Estimated or Actual CFM |  | Delta T |  | BTU Output
750 |  | 70 |  | 56700
|  | BTU Output (base on flow rate) |  | 71009.28
| Thermal Efficiency | 79.85%

## Fan Laws
Fan Laws & Capacitors
Fan Law 1.
New CFM= (new rpm x existing cfm)/existing rpm
New RPM=(new cfm X existing rpm) / existing cfm
New CFM | = | Existing RPM | Existing CFM | New RPM
1200 |  | 825 | 1000 | 990
New RPM= |  | Existing CFM | Existing RPM | New CFM
990 |  | 1000 | 825 | 1200
Fan Law 2.
Static Pressure
New s.p=existing s.p x (new RPM/existing RPM)^2
New Static Pressure | = | Exist S.P. | Existing RPM | New RPM
0.72 |  | 0.5 | 825 | 990
Fan Law 3.
Horsepower
New hp=existing hp x (new RPM/existing RPM)^3
New Horsepower | = | Existing HP | New RPM | Existing RPM
0.57024 |  | 0.33 | 990 | 825
Pulley fan RPM
|  | Diameter of | Diameter of
Fan RPM | = | Fan Pulley | Motor Pulley | Motor RPM
739.2857 |  | 7 | 3 | 1725
Calculate Belt Length
52.58 |  | Diameter of | Diameter of | CL-Shaft
Belt Length (in) | = | Fan Pulley | Motor Pulley | to Shaft
52.58" or 52 9/16" |  | 4 | 10 | 15
Capacitors
In Parallel-Add Capacitors together, Volts = lowest rated capacitor.
New µf | = | Cap1 µf | Cap2 µf | Cap3 µf
27.5 | = | 5 | 10 | 12.5
New Volts | = | Cap1 Volts | Cap2 Volts | Cap3 Volts
330 | = | 330 | 440 | 333
In Series, µf will be lower, Volts are added together.
New µf | = | Cap1 µf | Cap2 µf | Cap3 µf
7.1591 | = | 35 | 15 | 22.5
New Volts= | = | Cap1 Volts | Cap2 Volts | Cap3 Volts
1103 | = | 330 | 440 | 333

## Psychrometrics & Charging
Psychrometrics & Refrigerant Charging
Calculate Dew Point (Temp in °F)
|  |  |  | 23.89 |  | 17.625
Dew Point °F |  | Temperature |  | Humidity |  | 243.04
62.4413 | °F | 75 | °F | 65 | % | 1.1466
Calculate Wet Bulb From Dry Bulb & Humidity. (Temp in °F)*
Wet Bulb |  | Temp DB |  | Humidity
64.3967 | °F | 77 | °F | 50 | % | 25
*WB temp doesn't always match online calculator probably due to a rounding error, but usually off less than 1/2°
System Capacity Calc for Evaporator Coil-at sea level
|  |  | WB Supply Temp | 54.9 |  | 23.16 | BTU/Lb
|  |  | WB Return Temp | 64.4 | - | 29.61 | BTU/Lb
BTUs/Hr | = | CFM | X | ▲ht |  | 6.45 | ▲ht
23220 |  | 800 |  | 6.45
1.9 Tons |  | 12000 | @BTU's/ton |  |  | (4.5 X CFM X ▲ht)
*Used for manual calcs. Manual calcs for enthalpy are not as accurate as using psychrometric probes.
System Capacity Calc for Evaporator Coil-DB, Relative Humidity & Elevation
[6 empty] | 14.4193 | Baro Press (psia)
| Elevation | 525 | ft | RH %
| DB Supply Temp | 59 |  | 80 |  | 23.5682 | BTU/Lb
| DB Return Temp | 77 |  | 50 | - | 29.5109 | BTU/Lb
BTUs/Hr | = | CFM | X | ▲ht |  | 5.9427 | ▲ht
21393.6661 |  | 800 |  | 5.9427
1.8 Tons |  | 12000 | @BTU's/ton |  |  | (4.5 X CFM X ▲ht)
CFM based on Enthalpy and nominal system capacity.
CFM |  | ▲ht |  | Nominal BTU's
1346.1928 |  | 5.9427 |  | 36000 |  | CFM=BTU/(4.5 * ▲ht)
Calculate The Target Evaporator Air Temperature Split (°F) Range +- 3°F
|  | Return Air |  | Return Air
▲T |  | Dry Bulb |  | Wet Bulb
18.2 | °F | 77 | °F | 64.4 | °F
*If it's higher, then check for airflow issues and blower settings. If it's lower, then connect gauges.
Calculate Recovery Tank @ 80%
|  |  | Tank Tare Weight: | 16.6 |  | Liquid Density (130*F) Ref lb/ft^3
|  |  | Tank Water Capacity: | 46 |  |  | R-134a | 67.5
|  |  | Max Temperature: | 130°F |  |  | R-22 | 66.3
|  |  | Refrigerant Type: | R-410a |  |  | R-410a | 54.7
|  |  | Density: | 54.7 |  |  | R-404a | 53.18
|  |  | Total Weight (TW + Fill Weight) @ 80%: | 48.8074 | lbs. |  | R-407c | 62.28
|  |  | Refrigerant Weight (Fill Weight) @ 80%: | 32.2074 | lbs. |  | R-290 | 27.711
|  |  | Existing non-empty tank calc |  |  |  | R-12 | 74.6
|  |  | Total Tank weight before starting recovery: | 22 | Must be > Tank Tare Wt.
|  |  | Max. additional refrigerant | 26.8074 | lbs.
that can be added to the tank:
Calculate Superheat based on return air WB°F and OAT°F DB-Fixed Orifice
Superheat Target |  | OA Temp DB |  | Return Air Temp WB
11.6 | °F | 90 | °F | 64.4 | °F
Actual Total Superheat |  | SL Sat Temp |  | SL Clamp Temp
10 | °F | 40 | °F | 50 | °F | 1.6
Difference of 1.6 | °F | Charge OK
Tolerance +- 2° F
Calculate Subcooling-TXV
Subcooling Target |  | Target SC |  | Sat Temp |  | LLTemp
12 | °F | 16 | °F | 98 | °F | 86 | °F
Difference of -4 | °F | Recover Refrigerant |  |  |  | -4
Tolerance +- 3° F
Measure ΔT Across Evaporator Coil-After Confirming Proper SH or SC Charge
Range-Low |  | Range-High |  | Return Temp |  | Supply Temp
18 | °F | 21 | °F | 77 | °F | 59 | °F
ΔT 18 | °F | ΔT correct refrigerant level |  |  |  | 18
Range 18 °-21° ΔT
Compression Ratio
|  | Liquid Line |  | Suction Line
Compression Ratio |  | PSIG |  | PSIG |  | Altitude (ft.) |  | psia
(Lower ratio=more efficient) |  | 285 |  | 155 |  | 1000 |  | 14.1727
1.77 : 1 |  | 299.2 psia | / | 169.2 psia |  | Lower ratio=more efficient
Nitrogen Pressure/Temp Calculator
| Elevation (feet) | 60
| PSIA | 14.6642
| Start Temp °F | 80
| Start Pressure (psig) | 246
| End Temp °F | 80.4
| Adjusted Pressure (psig) | 246.1932
(Range 243.73-248.66 psig)
| End Pressure (psig) | 247
Pass
Chart
Chart

## Properties of Air
Properties of Air
Enthalpy Calculator (From Tdb and RH)
Acceptable accuracy (>99%) between 25°F to 100°F Tdb
|  | Return Air |  |  |  |  | Supply Air
|  | °F | °C | PSIA |  |  | °F | °C
| Dry bulb Tdb | 72.4 | 22.4444 | 14.5637 |  | Dry bulb Tdb | 52.1 | 11.1667
| RH (%) | 66.2 |  |  |  | RH (%) | 93.4
| Elevation | 250 |  |  |  | Elevation | 250
| Wet Bulb (from DB & Hum) | 64.4877 |  |  |  | Wet Bulb (from DB & Hum) | 50.7585
| Dew Point Tdp | 60.4812 | 15.8229 |  |  | Dew Point Tdp | 50.2523 | 10.1402
| Enthalpy (btu/lb) | 29.7756 |  |  |  | Enthalpy (btu/lb) | 20.9317
| Humidity Ratio | 0.011345 | 0.662 |  |  | Humidity Ratio | 0.0077748
| Gr. Moisture H20/lb DB | 79.4156 |  |  |  | Gr. Moisture H20/lb DB | 54.4236
| Sat. Pressure (psia) | 0.39411 |  |  |  | Sat. Pressure (psia) | 0.19252
| Specific Volume | 13.5531 | 0.662 |  |  | Specific Volume | 13.0363 | 0.934
| Partial Pressure | 0.31876 |  |  |  | Partial Pressure | 0.77696
| Air Density | 0.073784 |  |  |  | Air Density | 0.076709
|  | Actual CFM | 1600 |  | 63885.5851 | Delivered BTU'S
|  | Standard CFM | 1545.7 |  | 5.3238 | Delivered Tons
Total1-Sensible1=Latent1
|  | Total1 | 63676.4762 | (4.5 * CFM * DeltaHt)
|  | Sensible1 | 35078.4 | 1.08*cfm*(ReturnDB-SupplyDB)
|  | Latent1 | 28598.0762 | Total1-Sensible1
|  | Sensible Heat Ratio % | 55.0885
Total2-Sensible2=Latent2 (Based on Standard Air (SCFM))
|  | Total 2 | 61515.4558 | Total btu's based on standard air
|  | Sensible2 | 35078.4 | 1.08*cfm*(ReturnDB-SupplyDB)
|  | Latent2 | 26437.0558 | Total2-Sensible2
|  | Sensible Heat Ratio % | 57.0237
Total3=Latent3 + Sensible3
|  | Total3 | 62384.9342 | Latent3 + Sensible3
|  | Sensible3 | 35193.5949 | Sensible-using Air Density
|  | Latent3 | 27191.3393 | From hum ratio 0.68*CFM*ABS((lb H20ra-lb H20sa))
|  | Sensible Heat Ratio % | 56.4136
Total4-Based Air Density & Humidity Ratio
|  | Total4 | 63885.5851 | Total-using air density
|  | Sensible4 | 35193.5949 | Sensible-using Air Density
|  | Latent4 | 27191.3393 | From hum ratio 0.68*CFM*ABS((lb H20ra-lb H20sa))
|  | Sensible Heat Ratio % | 55.0885

## Duct Traverse
*Number of readings needed below based on Traverse Panel on the right
Calculate CFM from Pressure-Multiple Traverse Points |  |  |  |  | Calculate CFM from Pressure-Multiple Traverse Points |  |  |  | Traverse/Drill Points
| Rectangular Duct |  |  |  |  | Round Duct |  |  | Rectangular (In.) |  |  |  | Traverse/drill points (mm)
| Length (In.) |  | Width (In.) |  |  | Diameter (In.) |  |  | Width (In.) | 12 | 16, 62, 112, 152, 193, 244, 289 mm (7)
| 12 |  | 10 |  |  | 10 |  |  | Length (In.) | 10 | 13, 52, 93, 127, 161, 203, 241 mm (7)
| CFM |  | Avg. Ft/Min |  |  | CFM | Avg. Ft/Min
| 808.5635 |  | 970.2761 |  |  | 503.1341 | 922.4787 |  |  | Round (In.) |  |  | Circumference
| CFM |  | Static Press. | Ft/Min |  | CFM | Static Press. | Ft/Min | Outside diameter | 10 |  | 31 7/16" or 798 mm |  |  | 31.4159
1 | 782.7131 |  | 0.055 | 939.2558 | 1 | 436.8777 | 0.04 | 801 |  |  |  | Drill Point #2- | 42 mm | (from first hole)
2 | 775.5649 |  | 0.054 | 930.6779 | 2 | 507.606 | 0.054 | 930.6779 |  |  |  | Drill Point #3- | 85 mm | (from first hole)
3 | 789.7967 |  | 0.056 | 947.756 | 3 | 516.9207 | 0.056 | 947.756 |  | Round (In.) |  |  | 6 Traverse points (mm)
4 | 796.8172 |  | 0.057 | 956.1806 | 4 | 521.5156 | 0.057 | 956.1806 | Inside diameter | 6 | 5, 21, 49, 103, 132, 148 mm
5 | 817.5172 |  | 0.06 | 981.0206 | 5 | 535.0638 | 0.06 | 981.0206
6 | 775.5649 |  | 0.054 | 930.6779 | 6 | 507.606 | 0.054 | 930.6779
7 | 782.7131 |  | 0.055 | 939.2558 | 7 | 512.2845 | 0.055 | 939.2558 | Adjusted CFM for Temperature and Altitude.
8 | 789.7967 |  | 0.056 | 947.756 | 8 | 521.5156 | 0.057 | 956.1806 | Adjusted CFM |  | CFM (above) |  | AD Corr Factor | Temp (F°) |  | Alt. (Feet)
9 | 796.8172 |  | 0.057 | 956.1806 | 9 | 507.606 | 0.054 | 930.6779 | 511.5012 |  | 503.1 |  | 0.98358 | 74 |  | 250
10 | 782.7131 |  | 0.055 | 939.2558 | 10 | 516.9207 | 0.056 | 947.756
11 | 761.0671 |  | 0.052 | 913.2805 | 11 | 483.535 | 0.049 | 886.5445
12 | 824.3017 |  | 0.061 | 989.162 | 12 | 483.535 | 0.049 | 886.5445
13 | 907.8982 |  | 0.074 | 1089.4778 | 13 | 478.5756 | 0.048 | 877.4515
14 | 870.3135 |  | 0.068 | 1044.3762 | 14 | 488.4441 | 0.05 | 895.5452
15 | 738.7871 |  | 0.049 | 886.5445 | 15 | 493.3044 | 0.051 | 904.4563
16 | 738.7871 |  | 0.049 | 886.5445 | 16 | 498.1172 | 0.052 | 913.2805
17 | 731.2096 |  | 0.048 | 877.4515 | 17 | 493.3044 | 0.051 | 904.4563
18 | 746.2877 |  | 0.05 | 895.5452 | 18 | 502.884 | 0.053 | 922.0202
19 | 753.7136 |  | 0.051 | 904.4563 | 19 | 507.606 | 0.054 | 930.6779
20 | 761.0671 |  | 0.052 | 913.2805 | 20 | 498.1172 | 0.052 | 913.2805
21 | 753.7136 |  | 0.051 | 904.4563 | 21 | 493.3044 | 0.051 | 904.4563
22 | 746.2877 |  | 0.05 | 895.5452 | 22 | 483.535 | 0.049 | 886.5445
23 | 738.7871 |  | 0.049 | 886.5445 | 23 | 478.5756 | 0.048 | 877.4515
24 | 731.2096 |  | 0.048 | 877.4515 | 24 | 530.5862 | 0.059 | 972.8111
25 | 723.5528 |  | 0.047 | 868.2633 | 25 | 526.0704 | 0.058 | 964.5317
26 | 731.2096 |  | 0.048 | 877.4515 | 26 | 521.5156 | 0.057 | 956.1806
27 | 803.7764 |  | 0.058 | 964.5317 | 27 | 516.9207 | 0.056 | 947.756
28 | 796.8172 |  | 0.057 | 956.1806 | 28 | 512.2845 | 0.055 | 939.2558
29 | 782.7131 |  | 0.055 | 939.2558 | 29 | 507.606 | 0.054 | 930.6779
30 | 761.0671 |  | 0.052 | 913.2805 | 30 | 512.2845 | 0.055 | 939.2558
31 | 738.7871 |  | 0.049 | 886.5445
32 | 789.7967 |  | 0.056 | 947.756
33 | 782.7131 |  | 0.055 | 939.2558
34 | 775.5649 |  | 0.054 | 930.6779
35 | 789.7967 |  | 0.056 | 947.756
36 | 810.6759 |  | 0.059 | 972.8111
37 | 761.0671 |  | 0.052 | 913.2805
38 | 753.7136 |  | 0.051 | 904.4563
39 | 782.7131 |  | 0.055 | 939.2558
40 | 810.6759 |  | 0.059 | 972.8111
41 | 2213.847 |  | 0.44 | 2656.6165
42 | 692.0787 |  | 0.043 | 830.4945
43 | 782.7131 |  | 0.055 | 939.2558
44 | 789.7967 |  | 0.056 | 947.756
45 | 796.8172 |  | 0.057 | 956.1806
46 | 803.7764 |  | 0.058 | 964.5317
47 | 810.6759 |  | 0.059 | 972.8111
48 | 817.5172 |  | 0.06 | 981.0206
49 | 824.3017 |  | 0.061 | 989.162

## Conversions
Conversions
Inches to MM |  |  |  |  | Nearest Fraction
MM | = | Inches |  | (construction tape measure)
651.9926 | = | 25.669 | (25-11/16" or 2' 1-11/16")
MM | = | Feet |  | Inches | Fraction
3092.45 | = | 10 | ' | 1 | 0.75 | (121.75")
MM to inches-decimal
Inches | = | MM
11.811 | = | 300
MM to inches-nearest fraction (construction tape measure)
Inches | = | MM
25-11/16" | = | 652
2' 1-11/16" | or
25.669" | or
Temperature
Temp °C | < | Temp °F
35 | = | 95
Temp °F | < | Temp °C
77 | = | 25
Calculate Change in Copper Tubing
Change in Length (in) | = | Length (ft) |  | Temp Change
0-1/32" or 0' 1/32" |  | 10 |  | 30 | 0.03384
0.9 mm
Sizing for Domestic Hot Water-BTUH Input
| Desired Temperature | 140 | °F
| Inlet Water Temperature | 50 | °F
| Expected Flow Rate | 5 | GPM
| Required Input | 278437.5 | BTUH Input

## Pipe Bending
Pipe Bending | Enter the radius of the bender & degree of bed.
Answer is amount of gain(stretch) to be subtracted from measured length.
Radius of Bender | 127 | mm | (5 inches or 5") | 5
If using 127mm, enter 5 in inches below.
Radius of Bender | 5 | " | (5" or 0' 5")
Degree of Bend | 90 | °
Developed Length | 7.8525 | " | (7-7/8" or 0' 7-7/8")
K | 10 | " | (10" or 0' 10")
Gain | 2.1475 | " | (2-1/8" or 0' 2-1/8")
Gain2 | 2.1475 | " | (2-1/8" or 0' 2-1/8")
Standard Gains by Angle, based on a 5 inch radius bender.
10° | 0.0023866 | " | (0" or 0' 0")
15° | 0.007775 | " | (0" or 0' 0")
22.5° | 0.025999 | " | (0-1/32" or 0' 1/32")
30° | 0.061992 | " | (0-1/16" or 0' 1/16")
45° | 0.21589 | " | (0-3/16" or 0' 3/16")
60° | 0.5385 | " | (0-9/16" or 0' 9/16")
90° | 2.1475 | " | (2-1/8" or 0' 2-1/8")

## Boiler
Determining Boiler Efficiency
Clocking a Gas Meter
| Appliance Rated Efficiency (BTU's/Hr) | 86000
| BTU's Used-Oil or Gas BTU Ouput (BTU's/Hr) | 98000 |  | Drive Dial | 1 | Cubic Feet
| Appliance Steady State Efficiency (BTU's/Hr) | 87.76% |  | Seconds-1 revolution | 45
| Cycle Efficiency |  |  | Cubic Ft/Hour | 80 | ACFH (Actual Cubic Ft/Hour)
If meter pressure is above 1 psi and a higer elevation
|  |  |  | PSIG @ Meter | 2
|  |  |  | Elevation | 400 | Ft.
|  |  |  | PSIA | 14.4848
|  |  |  | Cubic Ft/Hour@ Burner Tip | 1.1217
|  |  |  | Flow Rate | 89.7377 | SCFH (Standard Cubic Ft/Hour)
@ 2 PSIG at the meter, customer burns 1.122 cubic feet/hr at the tip
and the adjusted flow rate (SCFH) is 89.74 Cubic Feet/Hour.
|  |  | BTU Output |  | Gas
|  |  |  | BTU content of gas | 1050 | 1050 (typical)
|  |  |  | Efficiency of Appliance | 80 | %
|  |  |  | BTU Output | 67200 | ACFH
|  |  |  | BTU Output | 75379.6664 | SCFH
Heating Oil
|  |  |  | BTU content of Oil | 140000 | 139,000/gallon (typical)
|  |  |  | Nozzle Firing Rate | 0.65 | @
|  |  |  | Pump Pressure | 150 | psi
|  |  |  | True Firing Rate | 0.8 | gph
|  |  |  | Efficiency of Appliance | 80 | %
|  |  |  | BTU Output | 89600

## Oil Line Calcs
Oil Line Calculations
Anticipated Vacuum
3/8 | "OD copper tube size | 0.0086
15 | GPH Flow rate (Gearset Capacity) for Fuel Unit (TGSC) Most single stage fuel units (Like Riello, Suntec, Beckett CleanCut, use 15-See Table)
10 | Ft. Lift (from bottom of suction line to the center of the fuel unit
20 | Ft. Horizontal length of fuel line
9.629 | Inches of Total Vacuum (anticipated). Does not include valves, filter, etc.
Anticipated Inlet Pressure (tank above fuel unit)
60 | In. Vertical length of fuel line (top fo tank to center of fuel pump)
2.1655 | PSI on fuel inlet (anticipated)
Within NFPA guidelines, no OSV needed.
Maximum amount of fuel line you can run (not to exceed). Single Pipe, Single Stage.
1/2 | "OD copper tube size | 0.00218
Suntec A7*** 3 gph-Current | Fuel Unit
15 | GPH Flow rate
Above | Tank Above/Below Pump
100 | Ft. Lift (from bottom of suction line to the center of the fuel unit
2477.0642 | Total Feet available. Does not include allowances for valves, filter, etc.
43.31 | psi pump inlet pressure. Exceeds NFPA guidelines (>3 psi) for inlet pressure, install OSV within 3' vertical height of center of fuel unit.
Maximum amount of fuel line you can run (not to exceed). Two Pipe or Oil Deaerator. |  |  |  |  | Riello pump vacuum-Single pipe 6", Two Pipe or Oil Deaerator 12"
3/8 | "OD copper tube size | 0.0086
Beckett A2EA | Fuel Unit
15 | GPH Flow rate (Gearset Capacity) for Fuel Unit (TGSC) Most single stage fuel units (Like Riello, Suntec, Beckett CleanCut, use 15-See Table)
Below | Tank Above/Below Pump
Single-Stage | Single Stage/Two Stage |  | 63.9535 | 122.093
5 | Ft. Lift (from bottom of suction line to the center of the fuel unit
63.9535 | Ft. Maximum length of supply tubing.
12 | @ 64 ft. Vacuum within manufacturer recommendations. Does not include valves, filter, etc.
psi pump inlet pressure. Exceeds NFPA guidelines (>3 psi) for inlet pressure, install OSV within 3' vertical height of center of fuel unit.
List of Fuel Pumps

## Pump Pressures
BTU Output of Heating Oil
ULSD | Type of Heating Oil | 138690 | BTU's
0.7 | Flow Rate in GPH
97083 | BTU output.
|  | Current Nozzle Size (gph) |  |  | Current Nozzle Pressure (psi) | Flow Rate | Standard Nozzle Sizes* |  | *Note, if you edit these nozzles, they must
| 1.5 |  |  | 140 |  | 1.7748 | 0.4 |  | remain in order, from lowest to highest,
[7 empty] | 0.5 | 0.4 | or calculations will break.
|  | Maximum Pump Pressure | 300 |  |  |  | 0.6 | 0.5
[7 empty] | 0.65 | 0.6
|  | Alternate Nozzle Size (gph) |  |  | Alt Nozzle Pressure (psi) | Flow Rate | 0.7 | 0.65
| 1.35 |  |  | 172.8395 |  | 1.7748 | 0.75 | 0.7
| 1.25 |  |  | 201.6 |  | 1.7748 | 0.85 | 0.75
| 1.2 |  |  | 218.75 |  | 1.7748 | 0.9 | 0.85
| 1.1 |  |  | 260.3306 |  | 1.7748 | 1 | 0.9
| 1 | [5 empty] | 1.1 | 1
| 0.9 | [5 empty] | 1.2 | 1.1
| 0.85 | [5 empty] | 1.25 | 1.2
| 0.75 | [5 empty] | 1.35 | 1.25
| 0.7 | [5 empty] | 1.5 | 1.35
| 0.65 | [5 empty] | 1.65 | 1.5
| 0.6 | [5 empty] | 1.75 | 1.65
| 0.5 | [5 empty] | 2 | 1.75
| 0.4 | [5 empty] | 2.25 | 2
[7 empty] | 2.5 | 2.25
[7 empty] | 2.75 | 2.5
[7 empty] | 3 | 2.75
[7 empty] | 3.25 | 3
[7 empty] | 3.5 | 3.25
[7 empty] | 4 | 3.5
[7 empty] | 4.5 | 4
[7 empty] | 5 | 4.5
[7 empty] | 5.5 | 5
[7 empty] | 6 | 5.5
[7 empty] | 6.5 | 6
[7 empty] | 7 | 6.5
[7 empty] | 7.5 | 7
[7 empty] | 8 | 7.5
[7 empty] | 8.5 | 8
[7 empty] | 9 | 8.5
[7 empty] | 9.5 | 9
[7 empty] | 10 | 9.5
[7 empty] | 11 | 10
[7 empty] | 12 | 11
[7 empty] | 13 | 12
[7 empty] | 14 | 13
[7 empty] | 15 | 14
[7 empty] | 16 | 15
[7 empty] | 17 | 16
[7 empty] | 18 | 17
[7 empty] | 19 | 18
[7 empty] | 20 | 19
20

## Delta T Evap Chart
Target Delta T Across the Evaporator Coil
<<Return< to Calcs

## SH Chart
<<<Return to Calcs

## Enthalpy Chart
Enthalpy in BTU per Pound of Dry Air |  | Liquid Density (130*F) Refrigerant lb/ft^3
Wet Bulb Temperature F |  |  | R-22 | 66.312
|  |  | R-134a | 67.46
35 | 13.01 |  | R-410a | 54.7
35.1 | 13.05 |  | R-404a | 53.18
35.2 | 13.1 |  | R-407c | 62.28
35.3 | 13.14 |  | R-290 | 27.711
35.4 | 13.48 |  | R-12 | 74.6
35.5 | 13.23
35.6 | 13.27
35.7 | 13.31
35.8 | 13.35
35.9 | 13.4
36 | 13.44
36.1 | 13.48
36.2 | 13.53
36.3 | 13.57
36.4 | 13.61
36.5 | 13.66
36.6 | 13.7
36.7 | 13.75
36.8 | 13.79
36.9 | 13.83
37 | 13.87
37.1 | 13.91
37.2 | 13.96
37.3 | 14
37.4 | 14.05
37.5 | 14.09
37.6 | 14.14
37.7 | 14.18
37.8 | 14.23
37.9 | 14.27
38 | 14.32
38.1 | 14.37
38.2 | 14.41
38.3 | 14.46
38.4 | 14.5
38.5 | 14.55
38.6 | 14.59
38.7 | 14.64
38.8 | 14.68
38.9 | 14.73
39 | 14.77
39.1 | 14.82
39.2 | 14.86
39.3 | 14.91
39.4 | 14.95
39.5 | 15
39.6 | 15.05
39.7 | 15.09
39.8 | 15.14
39.9 | 15.18
40 | 15.23
40.1 | 15.28
40.2 | 15.32
40.3 | 15.37
40.4 | 15.42
40.5 | 15.46
40.6 | 15.51
40.7 | 15.56
40.8 | 15.6
40.9 | 15.65
41 | 15.7
41.1 | 15.75
41.2 | 15.8
41.3 | 15.84
41.4 | 15.89
41.5 | 15.94
41.6 | 15.99
41.7 | 16.03
41.8 | 16.08
41.9 | 16.13
42 | 16.17
42.1 | 16.22
42.2 | 16.27
42.3 | 16.32
42.4 | 16.36
42.5 | 16.41
42.6 | 16.46
42.7 | 16.51
42.8 | 16.56
42.9 | 16.61
43 | 16.66
43.1 | 16.71
43.2 | 16.76
43.3 | 16.81
43.4 | 16.83
43.5 | 16.91
43.6 | 16.96
43.7 | 17
43.8 | 17.05
43.9 | 17.1
44 | 17.15
44.1 | 17.2
44.2 | 17.25
44.3 | 17.3
44.4 | 17.35
44.5 | 17.4
44.6 | 17.45
44.7 | 17.5
44.8 | 17.55
44.9 | 17.6
45 | 17.65
45.1 | 17.7
45.2 | 17.75
45.3 | 17.8
45.4 | 17.85
45.5 | 17.91
45.6 | 17.96
45.7 | 18.01
45.8 | 18.06
45.9 | 18.11
46 | 18.16
46.1 | 18.21
46.2 | 18.26
46.3 | 18.32
46.4 | 18.37
46.5 | 18.42
46.6 | 18.47
46.7 | 18.52
46.8 | 18.58
46.9 | 18.33
47 | 18.68
47.1 | 18.73
47.2 | 18.79
47.3 | 18.84
47.4 | 18.89
47.5 | 18.95
47.6 | 19
47.7 | 19.05
47.8 | 19.1
47.9 | 19.16
48 | 19.21
48.1 | 19.26
48.2 | 19.32
48.3 | 19.37
48.4 | 19.43
48.5 | 19.48
48.6 | 19.53
48.7 | 19.59
48.8 | 19.64
48.9 | 19.7
49 | 19.75
49.1 | 19.81
49.2 | 19.86
49.3 | 19.92
49.4 | 19.97
49.5 | 20.03
49.6 | 20.08
49.7 | 20.14
49.8 | 20.19
49.9 | 20.25
50 | 20.3
50.1 | 20.36
50.2 | 20.41
50.3 | 20.47
50.4 | 20.52
50.5 | 20.58
50.6 | 20.64
50.7 | 20.69
50.8 | 20.75
50.9 | 20.8
51 | 20.83
51.1 | 20.92
51.2 | 20.97
51.3 | 21.03
51.4 | 21.09
51.5 | 21.15
51.6 | 21.2
51.7 | 21.26
51.8 | 21.32
51.9 | 21.38
52 | 21.44
52.1 | 21.5
52.2 | 21.56
52.3 | 21.62
52.4 | 21.67
52.5 | 21.73
52.6 | 21.79
52.7 | 21.85
52.8 | 21.91
52.9 | 21.97
53 | 22.02
53.1 | 22.08
53.2 | 22.14
53.3 | 22.2
53.4 | 22.26
53.5 | 22.32
53.6 | 22.38
53.7 | 22.44
53.8 | 22.5
53.9 | 22.56
54 | 22.62
54.1 | 22.68
54.2 | 22.74
54.3 | 22.8
54.4 | 22.86
54.5 | 22.92
54.6 | 22.98
54.7 | 23.04
54.8 | 23.1
54.9 | 23.16
55 | 23.22
55.1 | 23.28
55.2 | 23.34
55.3 | 23.41
55.4 | 23.47
55.5 | 23.53
55.6 | 23.59
55.7 | 23.65
55.8 | 23.72
55.9 | 23.78
56 | 23.84
56.1 | 23.9
56.2 | 23.97
56.3 | 24.03
56.4 | 24.1
56.5 | 24.16
56.6 | 24.22
56.7 | 24.29
56.8 | 24.35
56.9 | 24.42
57 | 24.48
57.1 | 24.54
57.2 | 24.61
57.3 | 24.67
57.4 | 24.74
57.5 | 24.8
57.6 | 24.86
57.7 | 24.93
57.8 | 24.99
57.9 | 25.06
58 | 25.12
58.1 | 25.19
58.2 | 25.25
58.3 | 25.32
58.4 | 25.38
58.5 | 25.45
58.6 | 25.52
58.7 | 25.58
58.8 | 25.65
58.9 | 25.71
59 | 25.78
59.1 | 25.85
59.2 | 25.92
59.3 | 25.98
59.4 | 26.05
59.5 | 26.12
59.6 | 26.19
59.7 | 26.26
59.8 | 26.32
59.9 | 26.39
60 | 26.46
60.1 | 26.53
60.2 | 26.6
60.3 | 26.37
60.4 | 26.74
60.5 | 26.81
60.6 | 26.87
60.7 | 26.94
60.8 | 27.01
60.9 | 27.08
61 | 27.15
61.1 | 27.22
61.2 | 27.29
61.3 | 27.36
61.4 | 27.43
61.5 | 27.5
61.6 | 27.57
61.7 | 27.67
61.8 | 27.71
61.9 | 27.78
62 | 27.85
62.1 | 27.92
62.2 | 27.99
62.3 | 28.07
62.4 | 28.14
62.5 | 28.21
62.6 | 28.28
62.7 | 28.35
62.8 | 28.43
62.9 | 28.5
63 | 28.57
63.1 | 28.64
63.2 | 28.72
63.3 | 28.79
63.4 | 28.87
63.5 | 28.94
63.6 | 29.01
63.7 | 29.09
63.8 | 29.16
63.9 | 29.24
64 | 29.31
64.1 | 29.39
64.2 | 29.46
64.3 | 29.54
64.4 | 29.61
64.5 | 29.69
64.6 | 29.76
64.7 | 29.84
64.8 | 29.91
64.9 | 29.99
65 | 30.06
65.1 | 30.14
65.2 | 30.21
65.3 | 30.29
65.4 | 30.37
65.5 | 30.45
65.6 | 30.52
65.7 | 30.6
65.8 | 30.68
65.9 | 30.75
66 | 30.83
66.1 | 30.91
66.2 | 30.99
66.3 | 31.07
66.4 | 31.15
66.5 | 31.23
66.6 | 31.3
66.7 | 31.38
66.8 | 31.46
66.9 | 31.54
67 | 31.62
67.1 | 31.7
67.2 | 31.78
67.3 | 31.86
67.4 | 31.94
67.5 | 32.02
67.6 | 32.1
67.7 | 32.18
67.8 | 32.26
67.9 | 32.34
68 | 32.42
68.1 | 32.5
68.2 | 32.59
68.3 | 32.67
68.4 | 32.75
68.5 | 32.84
68.6 | 32.92
68.7 | 33
68.8 | 33.08
68.9 | 33.17
69 | 33.25
69.1 | 33.33
69.2 | 33.42
69.3 | 33.5
69.4 | 33.59
69.5 | 33.67
69.6 | 33.75
69.7 | 33.84
69.8 | 33.92
69.9 | 34.01
70 | 34.09
70.1 | 34.18
70.2 | 34.26
70.3 | 34.35
70.4 | 34.43
70.5 | 34.52
70.6 | 34.61
70.7 | 34.69
70.8 | 34.78
70.9 | 34.86
71 | 34.95
71.1 | 35.04
71.2 | 35.13
71.3 | 35.21
71.4 | 35.3
71.5 | 35.39
71.6 | 35.48
71.7 | 35.57
71.8 | 35.65
71.9 | 35.74
72 | 35.83
72.1 | 35.92
72.2 | 36.01
72.3 | 36.1
72.4 | 36.19
72.5 | 36.29
72.6 | 36.38
72.7 | 36.47
72.8 | 36.56
72.9 | 36.65
73 | 36.74
73.1 | 36.83
73.2 | 36.92
73.3 | 37.02
73.4 | 37.11
73.5 | 37.2
73.6 | 37.29
73.7 | 37.38
73.8 | 37.48
73.9 | 37.57
74 | 37.66
74.1 | 37.76
74.2 | 37.85
74.3 | 37.95
74.4 | 38.04
74.5 | 38.14
74.6 | 38.23
74.7 | 38.33
74.8 | 38.42
74.9 | 38.52
75 | 38.61
75.1 | 38.71
75.2 | 38.8
75.3 | 38.9
75.4 | 38.99
75.5 | 39.09
75.6 | 39.19
75.7 | 39.28
75.8 | 39.38
75.9 | 39.47
76 | 39.57
76.1 | 39.67
76.2 | 39.77
76.3 | 39.87
76.4 | 39.97
76.5 | 40.07
76.6 | 40.17
76.7 | 40.27
76.8 | 40.37
76.9 | 40.47
77 | 40.57
77.1 | 40.67
77.2 | 40.77
77.3 | 40.87
77.4 | 40.97
77.5 | 41.08
77.6 | 41.18
77.7 | 41.28
77.8 | 41.38
77.9 | 41.48
78 | 41.58
78.1 | 41.68
78.2 | 41.79
78.3 | 41.89
78.4 | 42
78.5 | 42.1
78.6 | 42.2
78.7 | 42.31
78.8 | 42.41
78.9 | 42.52
79 | 42.62
79.1 | 42.73
79.2 | 42.83
79.3 | 42.94
79.4 | 43.05
79.5 | 43.16
79.6 | 43.26
79.7 | 43.37
79.8 | 43.48
79.9 | 43.58
80 | 43.69
80.1 | 43.8
80.2 | 43.91
80.3 | 44.02
80.4 | 44.13
80.5 | 44.24
80.6 | 44.34
80.7 | 44.45
80.8 | 44.56
80.9 | 44.67
81 | 44.78
81.1 | 44.89
81.2 | 45
81.3 | 45.12
81.4 | 45.23
81.5 | 45.34
81.6 | 45.45
81.7 | 45.56
81.8 | 45.68
81.9 | 45.79
82 | 48.9
82.1 | 46.01
82.2 | 46.13
82.3 | 46.24
82.4 | 46.36
82.5 | 46.47
82.6 | 46.58
82.7 | 46.7
82.8 | 46.81
82.9 | 46.93
83 | 47.04
83.1 | 47.16
83.2 | 47.28
83.3 | 47.39
83.4 | 47.51
83.5 | 47.63
83.6 | 47.75
83.7 | 47.87
83.8 | 47.98
83.9 | 48.1
84 | 48.22
84.1 | 48.34
84.2 | 48.46
84.3 | 48.58
84.4 | 48.7
84.5 | 48.83
84.6 | 48.95
84.7 | 49.07
84.8 | 49.19
84.9 | 49.31
85 | 49.43
85.1 | 49.55
85.2 | 49.68
85.3 | 49.8
85.4 | 49.92
85.5 | 50.05
85.6 | 50.17
85.7 | 50.29
85.8 | 50.41
85.9 | 50.54

## Enthalpy Calcs
| 65 |  | https://excel-psychrometrics.com/#dry-bulb-wet-bulb
47
18.5864
Dry Bulb and Relative Humidity
Saturated Pressure-psia
74 | DB
0.6 | RH% | 60
| 0.41592 | psia
Humidity Ratio
DB | RH
74 | 0.6 | 60
0.010744
Enthalpy
DB | RH
74 | 0.6 | 60
29.5119
Dry Bulb and Dew Point Temp
Enthalpy
DB | DP
75 | 55.55
28.2683
Dry Bulb and Wet Bulb
Enthalpy
DB | 74
WB | 64.45
29.5149

## Traverse Points
Rectangular-Width | 304.8 | mm |  | Rectangular-Length | 254 | mm
23, 88, 152, 217, 282 mm |  |  | (5) | 19, 73, 127, 181, 235 mm |  |  | (5)
19, 72, 133, 172, 233, 286 mm |  |  | (6) | 15, 60, 111, 143, 194, 239 mm |  |  | (6)
16, 62, 112, 152, 193, 244, 289 mm |  |  | (7) | 13, 52, 93, 127, 161, 203, 241 mm |  |  | (7)
Less than 30" | Less than 63" |  | 63"+ | Less than 30" | Less than 63" |  | 63"+
23 | 19 |  | 16 | 19 | 15 |  | 13
88 | 72 |  | 62 | 73 | 60 |  | 52
152 | 133 |  | 112 | 127 | 111 |  | 93
217 | 172 |  | 152 | 181 | 143 |  | 127
282 | 233 |  | 193 | 235 | 194 |  | 161
| 286 |  | 244 |  | 239 |  | 203
|  |  | 289 |  |  |  | 241
Round-Inside Diameter |  | 152.4 | mm
5, 21, 49, 103, 132, 148 mm
3, 12, 23, 33, 55, 97, 119, 129, 141, 150 mm
Less than 10" | Greater than 10"
5 | 3
21 | 12
49 | 23
103 | 33
132 | 55
148 | 97
119
129
141
150

## Notes
Function RelativeHumidity(WetBulbTemp, DryBulbTemp, AtmosPress)
Rem Calculates the relative humidity from
Rem Wet bulb temperature WetBulbTemp deg C
Rem Dry Bulb temperature DryBulbTemp deg C
Rem Atmospheric pressure AtmosPress kPa
Rem This equation is taken from BS 4485, part 2, 1988, Appendix D
RelativeHumidity = 100# * (AirSatPress(WetBulbTemp) - 1000# * AtmosPress * (0.000666 * (DryBulbTemp - WetBulbTemp))) / AirSatPress(DryBulbTemp)
End Function
Function AirSatPress(AirTemp)
Rem Calculates the saturation vapour pressure of water (Pa) from temperature deg C
Rem This equation is taken from BS 4485, part 2, 1988, Appendix D
AirSatPress = 10 ^ (-2948.997118 / (AirTemp + 273.15) - 2.1836674 * Log(AirTemp + 273.15) - 0.000150474 * 10 ^ (-0.0303738468 * (AirTemp - 0.01)) + 0.00042873 * 10 ^ (4.76955 * (1 - 273.16 / (AirTemp + 273.15))) + 25.83220018)
End Function
Misc. Scratch Pad
PRESSURE = TOTAL-STATIC, THEN SQRT OF PRESSURE x 4005 x SQFT OF DUCT (FT LENGTH X FT WIDTH) OR pi*RADIUS^2
5.2556 | Alternate constant |  | 5.2561 | Standard constant
temp & pressure calc
0.77871
0.77871
TEMP |  | REL HUMIDITY
30 |  | 78
26.827
converting decimal to inches & fraction
0"
converting decimal to feet & inches & fraction
0' 0"

## Formulae
Formula-Do not alter or entire SS will break.
63.9535 | single stage tank below
122.093 | single stage tank above | IF(AND(B28="Single-Stage",B27="Below"),Formulae!B3,IF(AND(B28="Single-Stage",B27="Above"),Formulae!B4,IF(AND(B28="Two-Stage",B27="Below"),Formulae!B5,IF(AND(B28="Two-Stage",B27="Above"),Formulae!B6,"Data Missing"))))
100 | two stage tank below
100 | two stage tank above
Fuel Line Sizes
3/8
1/2
5/8
Above/Below
Above
Below
Stage-Fuel Unit
Single-Stage
Two-Stage
BTU Content of Heating Oil
ULSD | 138690
B20 | 126700
B100 | 119550

## Key
Unlock Sheet to add more fuel units. Make backup first.
TGSC
| Make/Model | Flow Rate 3450 rpm
| Beckett A2EA | 15
| Danfoss CFPH-BFPH | 15
| Riello-up to 2000 | 17
| Riello-Current | 15
| Suntec A7*** 3 GPH UNTIL 2000 | 17
| Suntec A7*** 3 gph-Current | 15
| Suntec A7*** 7 gph | 20
| Suntec B82** 3 gph | 21
| Suntec B89** 7gph | 25
| Suntec B8850 | 28
| Suntec B8851 | 33
| Suntec B8852 | 39
| Webster M34DK-3 | 17
Back to Oil Line Calcs